## Read Me
CD50 Intake Sheet (DRAFT)
One row per project fact. Fill the yellow Value column once; every CD50, CD90 and CD100 sheet reads from it.
Target format: Tesla V4 Templatized Plan Set (2026.09.21), 24x36, G/E/A/S numbering, plus SSC site info, general notes and specs.
Example values are from Cleveland TN CD100 Rev 1 (HP00125). Blank example cells were not on that set.
Tabs
Intake: the inputs. 'Needed by' says the first stage that needs the value.
Derived: values calculated from the inputs (currents, breaker size, SLD variant, fault current, weights, TSC rule).
Checks: pre-submission checks tied to Lessons Learned IDs. Formula checks show PASS / CHECK automatically; the rest are manual.
Lists: dropdown values. Edit here to change the choices.
Colors: yellow = input, green = calculated, do not type over green cells.

## Intake
Section | Field | Value | Units / format | Needed by | Source | Feeds | Notes
Project
Project | Applicant site name | CLEVELAND TN | Text | CD50 | HiON | Title block, G-001 title, placard | Shown on every sheet
Project | HiON site number | HP00125 | HP##### | CD50 | HiON | Title block | Use one format (HP00125 vs HP-00126 seen in sets)
Project | Tesla job number (JB-) |  | JB-XXXXXXX-00 | CD90 | Tesla | Title block | Template sheet ID block
Project | Tesla TRT number |  | Text | CD90 | Tesla | G-001 title
Project | APN (parcel number) |  | XXX-XXX-XXX-XXX | CD50 | County records | G-001 title
Project | Current stage | CD100 | List | CD50 | HiON | Title block, revision table
Project | Revision number / letter | 1 | Text | CD50 | SSC | Title block, revision table | A, B, C for review; 0 for permitting; 1+ after
Project | Revision description | REVISED PER CLIENT COMMENTS | Text | CD50 | SSC | Revision table
Project | Revision date | 2026-10-15 | Date | CD50 | SSC | Revision table
Site
Site | Site street address | 4011 APD 40 SW | Text | CD50 | HiON | Title block, G-001, placard
Site | City | CLEVELAND | Text | CD50 | HiON | Title block, G-001, placard
Site | State | TN | List | CD50 | HiON | Title block, code lookup, PE stamps
Site | ZIP | 37311 | Text | CD50 | HiON | Title block, placard
Site | County | BRADLEY | Text | CD50 | County records | G-001 site info
Site | AHJ (permitting jurisdiction) |  | Text | CD50 | HiON | G-001 codes, ADA type | City or county that issues the permit
Site | Property owner | EXAMPLE PROPERTY OWNER LLC | Text | CD50 | County records | G-001 site info, GN note 1
Site | Owner mailing address | 6155 STATE ROUTE 1241, HICKORY KY 42051 | Text | CD50 | County records | G-001 site info
Site | Host business / tenant |  | Text | CD50 | HiON | G-001 | e.g. Natural Grocers, Popeyes
Site | Latitude (NAD 83) | 35° 8' 11.67" N | DMS | CD50 | Google Earth / survey | G-001 site info
Site | Longitude (NAD 83) | 84° 54' 30.27" W | DMS | CD50 | Google Earth / survey | G-001 site info
Site | Ground elevation | 955 | ft AMSL | CD50 | Google Earth / survey | G-001 site info
Site | Survey available (with underground utilities) |  | List | CD90 | Surveyor | Existing site plan | L-036: survey must show underground lines and easements
Site | Public right of way next to equipment area |  | List | CD50 | Survey | E-101 check | L-007: cabinet clearance must stay out of public ROW
Codes
Codes | Building code edition (IBC) | 2018 | Year | CD50 | AHJ lookup | G-001 applicable codes | Verify adopted edition; L-042
Codes | Mechanical code edition (IMC) | 2018 | Year | CD50 | AHJ lookup | G-001 applicable codes
Codes | Electrical code edition (NEC) | 2017 | Year | CD50 | AHJ lookup | G-001 applicable codes, E sheets | Cleveland sheet shows 2017; other V4 sets show 2023. Verify for TN
Codes | ASCE 7 edition | 7-16 | Text | CD50 | AHJ lookup | G-001, S-501 design criteria
Codes | Other codes (state DOT, fire, energy) |  | Text | CD50 | AHJ lookup | G-001 | e.g. CDOT specifications on DTC
Team
Team | A&E firm | SSC, Inc. | Text | CD50 | HiON | Title block (A&E logo), G-001 team
Team | A&E site ID / project ID | SSC-32225 / P-074570 | Text | CD50 | SSC | G-001 team
Team | Project designer |  | Name | CD50 | SSC | G-001 team
Team | Electrical engineer of record (name, PE#) | SHELTON D. KEISLING, 128109 | Name, PE# | CD90 | SSC | G-001 team, stamp | PE number is state-specific
Team | Structural / civil engineer of record (name, PE#) | PETER C. LUNDQUIST, 127524 | Name, PE# | CD90 | SSC | G-001 team, stamp
Team | State certificate of authorization # | 701658608 | Text | CD90 | SSC | Title block
Team | HiON project manager / client manager | EVAN AUBRY | Name | CD50 | HiON | G-001 team
Team | Tesla project engineer (reviewer) | Mike Stern | Name | CD50 | Tesla | Review checklist, transmittal | See Tesla Contacts tab in Review Index
Equipment
Equipment | Cabinet model | V4 | List | CD50 | Tesla contract | All sheets: details, SLD, TSC rule | L-012: must match contract throughout
Equipment | Number of cabinets | 1 | Count | CD50 | Tesla contract | G-001 scope, E-101, SLD variant | DC-BUS wording only with multiple cabinets (L-038)
Equipment | Post model | V4 | List | CD50 | Tesla contract | Details, foundations, stall layout
Equipment | Number of posts (total) | 4 | Count | CD50 | Tesla contract | G-001, E-101 stall schedule, SLD | V4 cabinet supports up to 8 posts
Equipment | Cabinet nameplate rating | 625 kVA / 750 A | List | CD50 | Tesla contract | S-501 conduit window detail, weight | Tesla V4 template variants: 625 / 998 / 1247 kVA
Equipment | Commissioned input setting (kVA) | 499 | kVA | CD50 | HiON / Tesla | E-201 load schedule, cabinet spec table, derate table | Software-limited at commissioning; equal to nameplate if not derated
Equipment | Future cabinets planned | 0 | Count | CD50 | HiON | G-001 scope, conduit stub-ups | L-013: state future count, stub conduits for known future posts
Equipment | Future posts planned | 0 | Count | CD50 | HiON | E-101, stub-ups | L-013
Equipment | New light fixtures | 0 | Count | CD50 | HiON | E-201 lighting circuit, E-101 | Template includes (2) LGT
Equipment | Trash / recycle bins | 0 | Count | CD50 | HiON | E-101 | L-030: Tesla recommends
Electrical
Electrical | New or existing service | New service | List | CD50 | Utility | G-001 scope matrix, SLD | Also a Tesla checklist field
Electrical | Electric utility |  | Text | CD50 | Utility | Utility notes, scope matrix
Electrical | Service voltage | 480Y/277V 3PH 4W | Text | CD50 | Utility | SLD, panel schedule | Template assumes 480Y/277V
Electrical | Utility transformer size |  | kVA | CD90 | Utility | SLD AFC note, fault current | Template sample: 2000 kVA
Electrical | Transformer impedance |  | %Z | CD90 | Utility | SLD AFC note | Template sample: 5.75%; Tesla asked for this (L-039)
Electrical | Transformer and pad provided by | Utility | Text | CD50 | Utility | G-001 scope matrix | Pad size must match utility documents (L-041)
Electrical | Service equipment type | Panelboard | List | CD50 | SSC | SLD, E-101 tag SB-1 / PB1
Electrical | Service equipment tag | PB1 | Text | CD50 | SSC | SLD, schedules, placards | Template uses SB-1
Electrical | Service equipment bus / main rating | 800 | A | CD50 | SSC | SLD, panel schedule | Must be at least the cabinet breaker size
Electrical | Service equipment interrupting rating | 65 | kAIC | CD50 | SSC | Panel schedule | Tesla min 65 kAIC (L-039)
Electrical | CT cabinet with meter socket | Yes | List | CD50 | Utility | SLD, E-101
Electrical | Meter location | Utility rack | Text | CD50 | Utility | E-101
Electrical | Separate EVSE disconnect (not on cabinet side) | No | List | CD50 | SSC | SLD, E-101 | L-040: never attach to cabinet side; no EV-Lite or Duraline
Electrical | Grounding electrode | Ground rods | List | CD50 | SSC | E-501 grounding diagram
Electrical | AC feeder length, service to cabinet |  | ft | CD90 | Site plan | AC circuit schedule | Template max 600 ft
Electrical | Longest DC run, cabinet to post |  | ft | CD90 | Site plan | DC-POST schedule | Max 330 ft; contact Tesla beyond
Site layout
Site layout | Stall layout | Perpendicular, head-in | List | CD50 | HiON | E-101 | L-003, L-005
Site layout | Standard EV stall width | 9'-0" | ft-in | CD50 | Site plan | E-101 dimensions | Min 9 ft O.C. (L-032)
Site layout | Width of stall with post on one side | 10'-6" | ft-in | CD50 | Site plan | E-101 dimensions | V4: 10'-6" (L-032)
Site layout | Stall depth | 18'-0" | ft-in | CD50 | Site plan | E-101 dimensions | ADA min 18 ft
Site layout | Drive aisle width |  | ft | CD50 | Site plan | E-101 | Check AHJ for one-way aisles
Site layout | Accessible EV stalls | 1 | Count | CD50 | AHJ / ADA | E-101 stall schedule, A-501
Site layout | Accessible stall detail | IBC & ADA - standard | List | CD50 | AHJ | A-501 detail pick | CBC only in California
Site layout | Accessible post tag |  | Text | CD50 | Site plan | E-101 stall schedule | Template sample: 2E
Site layout | Bollards (total) | 10 | Count | CD50 | Site plan | G-001 scope, E-101 | L-010: every post, both sides recommended; verify count vs details
Site layout | Signs | 1 ADA sign with bollard | Text | CD50 | AHJ | G-001 scope, A-501 | L-008: only ADA sign unless AHJ requires; prefer light pole
Site layout | Restriping needed |  | List | CD50 | Site plan | E-101
Structural
Structural | Post foundation | Cast-in-place, 107 mph max | List | CD50 | SSC | S-501/502 detail pick | Cast-in-place only (L-037)
Structural | Design wind speed (ultimate) |  | mph | CD90 | ASCE hazard tool | S-501 design criteria, foundation pick
Structural | Wind exposure |  | List | CD90 | ASCE hazard tool | S-501
Structural | Risk category | II | List | CD90 | SEOR | S-501
Structural | Ground snow load |  | psf | CD90 | ASCE hazard tool | S-501, pad type
Structural | Cabinet pad section | No-snow | List | CD90 | SEOR | S-501 pad detail
Structural | Seismic site class | D | List | CD90 | Geotech / default | S-501 | Template default D
Structural | Seismic design category |  | Text | CD90 | ASCE hazard tool | S-501
Structural | Allowable soil bearing pressure | 1500 | psf | CD90 | Geotech / default | S-501 | Template assumes 1,500 psf
Schedule
Schedule | Expected equipment delivery |  | Date | CD90 | HiON | Tesla Design Review Checklist | Delivery form needs 4 weeks lead
Schedule | Planned construction start |  | Date | CD90 | HiON | Tesla Design Review Checklist
Schedule | Planned commissioning request |  | Date | CD90 | HiON | Tesla Design Review Checklist
Schedule | Open to public |  | Date | CD90 | HiON | Tesla Design Review Checklist

## Derived
Value | Result | Units | How it is calculated
Cabinet nameplate kVA |  | kVA | From the nameplate choice
Cabinet nameplate max AC input |  | A | From the nameplate choice
Cabinet weight for pad design |  | lbs | Tesla V4 template S-501: 2,337 lbs (4-post), 2,712 lbs (8-post). L-037
Commissioned AC input current |  | A | kVA x 1000 / (480 V x 1.732)
Derated below nameplate? |  |  | Yes means the set needs Tesla's derate table (L-039)
Minimum cabinet breaker (125%) |  | A | Continuous load x 1.25
Cabinet breaker size (next standard) |  | A | Next standard size per NEC 240.6
Tesla SLD sheet to start from |  |  | Tesla V4 template variants
Available fault current at secondary |  | A | Infinite primary assumption, as in the Tesla template AFC note
Fault-current-limiting fuses needed? |  |  | Cabinet SCCR is 34 kA; template adds (3) Mersen A4BQ fuses when AFC is higher
Tesla System Controller needed? |  |  | L-001: none with V4 cabinet; V3/V3.5 on its own rack, 15/2 breaker
Neutral to cabinet? |  |  | V4 cabinet is 3-wire (L-039)
Posts per cabinet |  |  | V4 cabinet supports up to 8
DC-POST circuits |  |  | One 4" conduit per post: (4) 600 kcmil AL, EGC, Tesla signal wire (L-038)
G-001 title line |  |  | Template title format
G-001 scope: posts
G-001 scope: cabinets
G-001 scope: service
G-001 scope: bollards

## Checks
Lesson | Check | Result | How
L-001 | TSC shown only when Derived says it is needed (none with V4) | MANUAL | Search the set for 'system controller' (Golden Rev 2 cover still lists one with a V4 cabinet)
L-012 | Cabinet and post model match the contract on every sheet | MANUAL | Elevations, details, dims, footprints
L-039 | Service equipment rating covers the cabinet breaker |  | Service rating >= derived breaker size
L-039 | Derate table shown when derated |  | Manual when derated: Tesla derate table on SLD sheet
L-039 | Cabinet rating labeled the same on every sheet | MANUAL | Cleveland Rev 1 shows 500 A, 600 A and 499 kVA on different sheets
L-039 | Fault current known and below 34 kA, or fuses shown |  | Needs transformer kVA and %Z
L-039 | Service equipment at least 65 kAIC
L-037 | Pad design uses the right cabinet weight | MANUAL | Compare detail weight with Derived cabinet weight (Cleveland shows 2,420 lbs)
L-032 | Standard stall width at least 9 ft; post-side stall 10'-6" (V4) | MANUAL | Dimension both on E-101
L-031 | Post cable terminus centered in stall and dimensioned | MANUAL
L-033 | ADA stall and aisle max 2% slope shown | MANUAL | Grading or spot elevations
L-034 | ADA details: 30x48 clear space, 48" max reach, post flush | MANUAL | Use A-501 detail chosen on Intake
L-010 | Bollard count matches scope and details | MANUAL | Compare with Intake bollards
L-035 | Clearances: cabinet 3 ft sides, 5 ft front; transformer clear of shrubs | MANUAL
L-036 | Survey shows underground lines and easements at equipment
L-007 | Cabinet clearance outside public right of way
L-040 | No EV-Lite or Duraline; nothing mounted on cabinet side | MANUAL
L-041 | Utility point of connection shown; transformer pad matches utility | MANUAL
L-042 | Code editions match AHJ adoption | MANUAL | Verify Intake code rows
L-042 | Sheet index matches sheets; no references to missing sheets | MANUAL | Cleveland C-3.0 points to 'Sheet CD-2'
L-004 | Every plan to scale with scale bar and north arrow | MANUAL
L-013 | Future cabinets and posts stated; stub-ups shown
L-022 | Design Review Checklist filled and attached with CD90 | MANUAL | Schedule tab dates feed it
L-021 | Send to Tesla as attachments, not Drive or Dropbox links | MANUAL
| DC run lengths within 330 ft |  | Contact Tesla if longer
Posts per cabinet at most 8

## Lists
YesNo | States | CabinetModel | PostModel | Nameplate | ServiceType | ServiceEquip | StdOCPD | StallLayout | ADAType | Foundation | PadType | Grounding | Stage | RiskCat | Exposure | SiteClass
Yes | AL | V4 | V4 | 625 kVA / 750 A | New service | Panelboard | 400 | Perpendicular, head-in | IBC & ADA - on the line | Cast-in-place, 107 mph max | No-snow | Ground rods | CD50 | I | B | A
No | AK | V3.5 | V3 | 998 kVA / 1200 A | Existing service | Switchboard | 450 | Perpendicular, back-in | IBC & ADA - standard | Cast-in-place, 135 mph max | Snow country | Concrete-encased electrode (CIP pads only) | CD90 | II | C | B
| AZ | V3 |  | 1247 kVA / 1500 A |  |  | 500 | Pull-through (reverse-in preferred) | IBC & ADA - van | Continuous cast-in-place, 107 mph max |  | Ground ring | CD100 | III | D | C
| AR | [5 empty] | 600 | Angled (needs Tesla OK; not with one-way V4) | CBC (California) - van & standard | Continuous cast-in-place, 135 mph max |  |  |  | IV |  | D
| CA | [5 empty] | 700 | [8 empty] | E
| CO | [5 empty] | 800 | [8 empty] | F
| CT | [5 empty] | 1000
| DE | [5 empty] | 1200
| FL | [5 empty] | 1600
| GA | [5 empty] | 2000
| HI | [5 empty] | 2500
| ID | [5 empty] | 3000
| IL | [5 empty] | 4000
IN
IA
KS
KY
LA
ME
MD
MA
MI
MN
MS
MO
MT
NE
NV
NH
NJ
NM
NY
NC
ND
OH
OK
OR
PA
RI
SC
SD
TN
TX
UT
VT
VA
WA
WV
WI
WY